## Reporte fugas
Procedure for using the UE SYSTEMS INC. ULTRAPROBE 3000, 9000 or 10000 to locate and roughly measure gas leakage in compressed gas systems.
Use the Scanning Module to conduct the broad scanning and to pinpoint the gas leaks. The Scanning Module with the rubber focusing probe should be held 15 inches away from the point of the leakage.
Notice: The values presented in the tables are not stated as factual CFM measurements. These tables are provided solely for convenience and should only be used as a general guideline.
* Factors such as turbulence, leak orifice configuration, pressure, moisture and instrument sensitivity can affect your results *
Leak on Compressors room
# | Zone | Type | Intermitencia | Decibels | Pressure | Description | Date | ACFM | Calculo | Diferencia
1 | Compressor Room N°1 | Pipe | 100% | 93 | 50 | Leak on Economat No. 1 flange gasket | 2020-11-17 | 7.905 | 7.8136 | 0.091424
2 | Compressor room N°1 | Pipe | 100% | 100 | 50 | Leak on hot low pressure pipe flange near Centac 1 compressor discharge | 2020-11-17 | 8.5 | 8.8343 | -0.33432
3 | Compressor room N°1 | Pipe | 100% | 68 | 50 | Leak on Centac 1 compressor discharge by-pass valve flange | 2020-11-17 | 5.78 | 4.6004 | 1.1796
4 | Compressor room N°1 | Pipe | 100% | 70 | 50 | Leak on Centac 1 compressor discharge by-pass valve flange | 2020-11-17 | 5.95 | 4.8317 | 1.1183
5 | Compressor room N°1 | Accessories | 100% | 80 | 90 | Leak on Ingersoll Rand Electropneumatic Positioner Gasket in Centac 6 Compressor | 2020-11-17 | 8.8 | 5.9589 | 2.8411
6 | Compressor room N°1 | Accessories | 100% | 64 | 90 | Leak on Centac 6 compressor blow-off pipe top flange gasket | 2020-11-17 | 7.04 | 4.3251 | 2.7149
7 | Compressor room N°1 | Accessories | 100% | 63 | 90 | Leak on Centac 6 compressor blow-off pipe bottom flange gasket | 2020-11-17 | 6.93 | 4.2284 | 2.7016
8 | Compressor room N°1 | Accessories | 100% | 67 | 90 | Leak on Centac 6 compressor discharge pipe flange gasket leak | 2020-11-17 | 7.37 | 4.6192 | 2.7508
9 | Compressor room N°1 | Accessories | 100% | 68 | 90 | Leak by porosity in pipe weld from Centac 6 compressor 5in discharge pipe | 2020-11-17 | 7.48 | 4.7185 | 2.7615
10 | Compressor room N°1 | Accessories | 100% | 68 | 90 | Leak on Centac 6 compressor discharge pipe flange packing | 2020-11-17 | 7.48 | 4.7185 | 2.7615
11 | Compressor room N°1 | Accessories | 100% | 65 | 90 | Leak on 2in relief valve in Centac 6 compressor discharge line | 2020-11-17 | 7.15 | 4.4225 | 2.7275
12 | Compressor room N°1 | Accessories | 100% | 69 | 90 | Leak on Centac 6 Compressor Discharge Pipe Weld | 2020-11-17 | 7.59 | 4.8185 | 2.7715
13 | Compressor room N°1 | Accessories | 100% | 70 | 50 | Leak on Centac 1 compressor discharge 7in discharge pipe flange gasket | 2020-11-17 | 5.95 | 4.8317 | 1.1183
14 | Compressor room N°1 | Accessories | 100% | 90 | 50 | Leaks on Centac 1 Compressor Blow Off 6 '' Pipe Flange Gasket | 2020-11-17 | 7.65 | 7.3919 | 0.25809
15 | Compressor room N°1 | Accessories | 100% | 103 | 50 | Leak on flange gasket before 6in pipeline by-pass valve (blow off) on Centac 1 compressor | 2020-11-17 | 8.755 | 9.2874 | -0.53235
16 | Compressor room N°1 | Accessories | 100% | 105 | 50 | Hole on drain hose from Centac 1 compressor | 2020-11-17 | 8.925 | 9.5945 | -0.66951
17 | Compressor room N°1 | Accessories | 100% | 70 | 90 | Broken hose in connection to Centac 5 compressor FRL filter | 2020-11-17 | 7.7 | 4.9191 | 2.7809
18 | Compressor room N°1 | Accessories | 100% | 63 | 90 | Leak on blow gun nozzle from Dryer 1 | 2020-11-17 | 6.93 | 4.2284 | 2.7016
19 | Compressor room N°1 | Accessories | 100% | 55 | 90 | Leak on Centac 5 compressor discharge pipe flange mismatch | 2020-11-17 | 6.05 | 3.4792 | 2.5708
20 | Compressor room N°1 | Accessories | 100% | 69 | 90 | Leak on Ingersoll Rand electropneumatic positioner Gasket in Centac 5 Compressor | 2020-11-17 | 7.59 | 4.8185 | 2.7715
21 | Compressor room N°1 | Accessories | 100% | 92 | 50 | Leak on Filter drain near outlet and Centac 6 compressor | 2020-11-17 | 7.82 | 7.672 | 0.14804
22 | Compressor room N°2 | Pipe | 100% | 100 | 50 | Economat 2 flange leak in 20in tubing | 2020-11-17 | 8.5 | 8.8343 | -0.33432
23 | Compressor room N°2 | Pipe | 100% | 90 | 50 | Economat 2 flange leak in 20in tubing | 2020-11-17 | 7.65 | 7.3919 | 0.25809
24 | Compressor room N°2 | Accessories | 100% | 63 | 90 | Centac 3 compressor drain quick coupler leak | 2020-11-17 | 6.93 | 4.2284 | 2.7016
25 | Compressor room N°2 | Accessories | 100% | 65 | 90 | Centac 3 compressor drain quick coupler leak | 2020-11-17 | 7.15 | 4.4225 | 2.7275
26 | Compressor room N°2 | Accessories | 100% | 80 | 90 | Centac 3 Compressor Electropneumatic Positioner Filter Cap Leak | 2020-11-17 | 8.8 | 5.9589 | 2.8411
27 | Compressor room N°2 | Accessories | 100% | 65 | 50 | Ingersoll Rand Electropneumatic Positioner Gasket Leak in Centac 2 Compressor | 2020-11-17 | 5.525 | 4.2623 | 1.2627
28 | Compressor room N°2 | Accessories | 100% | 83 | 50 | Centac 2 compressor discharge pipe flange packing leak | 2020-11-17 | 7.055 | 6.4456 | 0.60941
29 | Compressor room N°2 | Accessories | 100% | 73 | 50 | Centac 2 compressor discharge pipe flange packing leak | 2020-11-17 | 6.205 | 5.1872 | 1.0178
30 | Compressor room N°2 | Accessories | 100% | 85 | 50 | Centac 2 compressor discharge pipe expansion joint gasket leak | 2020-11-17 | 7.225 | 6.7106 | 0.51445
31 | Compressor room N°2 | Accessories | 100% | 65 | 90 | 1/4 "hose OD fitting leak in Dryer 4 drain (above room 2) | 2020-11-17 | 7.15 | 4.4225 | 2.7275
32 | Compressor room N°1 | Accessories | 100% | 60 | 50 | 2in butterfly valve handle leak in dryer 2 | 2020-11-17 | 5.1 | 3.7225 | 1.3775
[8 empty] | 232.635 | 181.6987 | 50.9363
[8 empty] | Dif: | 21.9%

## Calculo coeficiente
Caoeficiente multiplicador |  |  |  | Coeficiente exponencial
| Coeficiente fugas ultrasonido (dB) |  |  |  | Coeficiente fugas ultrasonido (dB)
Presión (psi) | Coef. Multiplicador | Regresión Polinomica |  | Presión (psi) | Coef. Exp. | Regresión Polinomica
10 | 0.0004 | 0.00023695 |  | 10 | 2.0766 | 2.0727
25 | 0.001 | 0.001054 |  | 25 | 1.9185 | 1.9153
50 | 0.0031 | 0.003651 |  | 50 | 1.6865 | 1.6919
75 | 0.0082 | 0.0077922 |  | 75 | 1.4978 | 1.5174
100 | 0.014 | 0.013478 |  | 100 | 1.4004 | 1.3917
125 | 0.02 | 0.020707 |  | 125 | 1.3399 | 1.3149
150 | 0.0297 | 0.029481 |  | 150 | 1.2712 | 1.287
| Correlacion | 0.99909 |  |  | Correlacion | 0.99877
Formula cfm en funcion de dB y psig=
Ejm:
|  | dB | psig | Leak CFM
|  | 16.7 | 30 | 0.2778
Note on B3: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Tomado de UE systems
Note on F3: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Tomado de UE systems

## Tabla UE
Sensitivity | 150 PSI | 125PSI | 100 PSI | 75 PSI | 50 PSI | 25 PSI | 10 PSI
dB Reading | Leak CFM | Leak CFM | Leak CFM | Leak CFM | Leak CFM | Leak CFM | Leak CFM
1 | 0.0297 | 0.02 | 0.014 | 0.0082 | 0.0031 | 0.001 | 0.0004
2 | 0.071685 | 0.050627 | 0.036956 | 0.023158 | 0.0099781 | 0.0037803 | 0.0016872
3 | 0.12003 | 0.087162 | 0.065206 | 0.042506 | 0.019771 | 0.0082292 | 0.0039161
4 | 0.17302 | 0.12815 | 0.097556 | 0.0654 | 0.032117 | 0.014291 | 0.007117
5 | 0.22977 | 0.17281 | 0.13334 | 0.091355 | 0.046792 | 0.021927 | 0.011312
6 | 0.2897 | 0.22064 | 0.17213 | 0.12004 | 0.063638 | 0.031109 | 0.016518
7 | 0.35241 | 0.27125 | 0.2136 | 0.15122 | 0.082531 | 0.041814 | 0.02275
8 | 0.4176 | 0.3244 | 0.25752 | 0.1847 | 0.10338 | 0.054023 | 0.03002
9 | 0.48505 | 0.37986 | 0.3037 | 0.22033 | 0.12609 | 0.06772 | 0.038339
10 | 0.55457 | 0.43745 | 0.35199 | 0.258 | 0.15061 | 0.08289 | 0.047716
11 | 0.626 | 0.49704 | 0.40225 | 0.29759 | 0.17688 | 0.09952 | 0.058159
12 | 0.69922 | 0.5585 | 0.45437 | 0.33901 | 0.20483 | 0.1176 | 0.069677
13 | 0.77411 | 0.62173 | 0.50827 | 0.38219 | 0.23444 | 0.13712 | 0.082276
14 | 0.85058 | 0.68664 | 0.56385 | 0.42706 | 0.26565 | 0.15807 | 0.095964
15 | 0.92855 | 0.75314 | 0.62105 | 0.47355 | 0.29843 | 0.18044 | 0.11075
16 | 1.0079 | 0.82116 | 0.67979 | 0.52161 | 0.33274 | 0.20422 | 0.12663
17 | 1.0887 | 0.89065 | 0.74003 | 0.57119 | 0.36856 | 0.22941 | 0.14362
18 | 1.1707 | 0.96155 | 0.8017 | 0.62224 | 0.40586 | 0.256 | 0.16172
19 | 1.254 | 1.0338 | 0.86476 | 0.67473 | 0.44461 | 0.28398 | 0.18093
20 | 1.3385 | 1.1073 | 0.92916 | 0.72861 | 0.48478 | 0.31335 | 0.20127
21 | 1.4242 | 1.1821 | 0.99486 | 0.78385 | 0.52636 | 0.34409 | 0.22273
22 | 1.5109 | 1.2582 | 1.0618 | 0.84042 | 0.56932 | 0.37622 | 0.24532
23 | 1.5988 | 1.3354 | 1.13 | 0.89828 | 0.61364 | 0.40971 | 0.26904
24 | 1.6876 | 1.4138 | 1.1994 | 0.9574 | 0.65931 | 0.44456 | 0.2939
25 | 1.7775 | 1.4932 | 1.27 | 1.0178 | 0.7063 | 0.48078 | 0.31991
26 | 1.8684 | 1.5738 | 1.3417 | 1.0793 | 0.7546 | 0.51835 | 0.34705
27 | 1.9602 | 1.6554 | 1.4145 | 1.1421 | 0.80419 | 0.55728 | 0.37534
28 | 2.053 | 1.7381 | 1.4884 | 1.2061 | 0.85505 | 0.59755 | 0.40479
29 | 2.1466 | 1.8218 | 1.5634 | 1.2711 | 0.90719 | 0.63916 | 0.43539
30 | 2.2412 | 1.9064 | 1.6394 | 1.3374 | 0.96056 | 0.68211 | 0.46714
31 | 2.3366 | 1.9921 | 1.7164 | 1.4047 | 1.0152 | 0.7264 | 0.50006
32 | 2.4328 | 2.0786 | 1.7945 | 1.4731 | 1.071 | 0.77202 | 0.53414
33 | 2.5298 | 2.1661 | 1.8735 | 1.5426 | 1.1281 | 0.81897 | 0.56939
34 | 2.6277 | 2.2545 | 1.9535 | 1.6131 | 1.1863 | 0.86725 | 0.6058
35 | 2.7263 | 2.3438 | 2.0344 | 1.6847 | 1.2458 | 0.91684 | 0.64339
36 | 2.8257 | 2.434 | 2.1163 | 1.7573 | 1.3064 | 0.96776 | 0.68215
37 | 2.9259 | 2.525 | 2.1991 | 1.8309 | 1.3682 | 1.02 | 0.72208
38 | 3.0268 | 2.6169 | 2.2827 | 1.9055 | 1.4311 | 1.0735 | 0.7632
39 | 3.1284 | 2.7096 | 2.3673 | 1.9811 | 1.4952 | 1.1284 | 0.8055
40 | 3.2307 | 2.803 | 2.4527 | 2.0577 | 1.5604 | 1.1845 | 0.84898
41 | 3.3337 | 2.8973 | 2.539 | 2.1352 | 1.6268 | 1.242 | 0.89365
42 | 3.4374 | 2.9924 | 2.6262 | 2.2137 | 1.6942 | 1.3008 | 0.93951
43 | 3.5418 | 3.0883 | 2.7142 | 2.2931 | 1.7628 | 1.3608 | 0.98655
44 | 3.6468 | 3.1849 | 2.803 | 2.3734 | 1.8325 | 1.4222 | 1.0348
45 | 3.7525 | 3.2822 | 2.8926 | 2.4547 | 1.9033 | 1.4849 | 1.0842
46 | 3.8588 | 3.3803 | 2.983 | 2.5368 | 1.9752 | 1.5488 | 1.1349
47 | 3.9658 | 3.4792 | 3.0742 | 2.6199 | 2.0481 | 1.6141 | 1.1867
48 | 4.0733 | 3.5787 | 3.1662 | 2.7038 | 2.1221 | 1.6806 | 1.2397
49 | 4.1815 | 3.6789 | 3.259 | 2.7886 | 2.1972 | 1.7484 | 1.294
50 | 4.2903 | 3.7799 | 3.3525 | 2.8743 | 2.2734 | 1.8175 | 1.3494
51 | 4.3997 | 3.8815 | 3.4467 | 2.9608 | 2.3506 | 1.8879 | 1.406
52 | 4.5096 | 3.9838 | 3.5418 | 3.0482 | 2.4289 | 1.9595 | 1.4639
53 | 4.6201 | 4.0868 | 3.6375 | 3.1364 | 2.5081 | 2.0325 | 1.523
54 | 4.7312 | 4.1905 | 3.734 | 3.2255 | 2.5885 | 2.1067 | 1.5832
55 | 4.8429 | 4.2948 | 3.8312 | 3.3153 | 2.6698 | 2.1822 | 1.6447
56 | 4.9551 | 4.3997 | 3.9291 | 3.406 | 2.7522 | 2.2589 | 1.7074
57 | 5.0679 | 4.5053 | 4.0277 | 3.4975 | 2.8356 | 2.3369 | 1.7714
58 | 5.1811 | 4.6116 | 4.127 | 3.5898 | 2.92 | 2.4162 | 1.8365
59 | 5.295 | 4.7184 | 4.227 | 3.683 | 3.0054 | 2.4968 | 1.9029
60 | 5.4093 | 4.8259 | 4.3276 | 3.7768 | 3.0918 | 2.5786 | 1.9705
61 | 5.5242 | 4.9339 | 4.429 | 3.8715 | 3.1792 | 2.6617 | 2.0393
62 | 5.6396 | 5.0426 | 4.531 | 3.967 | 3.2676 | 2.746 | 2.1093
63 | 5.7554 | 5.1519 | 4.6337 | 4.0632 | 3.357 | 2.8316 | 2.1806
64 | 5.8718 | 5.2618 | 4.737 | 4.1602 | 3.4473 | 2.9185 | 2.2531
65 | 5.9887 | 5.3722 | 4.841 | 4.2579 | 3.5387 | 3.0066 | 2.3268
66 | 6.1061 | 5.4832 | 4.9456 | 4.3564 | 3.631 | 3.096 | 2.4017
67 | 6.2239 | 5.5948 | 5.0508 | 4.4556 | 3.7242 | 3.1866 | 2.4779
68 | 6.3422 | 5.707 | 5.1567 | 4.5556 | 3.8185 | 3.2784 | 2.5553
69 | 6.461 | 5.8197 | 5.2632 | 4.6563 | 3.9136 | 3.3716 | 2.634
70 | 6.5803 | 5.933 | 5.3704 | 4.7578 | 4.0098 | 3.4659 | 2.7139
71 | 6.7 | 6.0469 | 5.4781 | 4.8599 | 4.1069 | 3.5616 | 2.795
72 | 6.8202 | 6.1613 | 5.5865 | 4.9628 | 4.2049 | 3.6584 | 2.8774
73 | 6.9408 | 6.2762 | 5.6954 | 5.0664 | 4.3038 | 3.7565 | 2.961
74 | 7.0619 | 6.3917 | 5.805 | 5.1707 | 4.4037 | 3.8559 | 3.0458
75 | 7.1835 | 6.5077 | 5.9151 | 5.2757 | 4.5046 | 3.9564 | 3.1319
76 | 7.3054 | 6.6242 | 6.0259 | 5.3814 | 4.6063 | 4.0583 | 3.2193
77 | 7.4279 | 6.7412 | 6.1372 | 5.4878 | 4.709 | 4.1613 | 3.3079
78 | 7.5507 | 6.8588 | 6.2491 | 5.5949 | 4.8126 | 4.2656 | 3.3977
79 | 7.674 | 6.9769 | 6.3616 | 5.7027 | 4.9171 | 4.3712 | 3.4888
80 | 7.7977 | 7.0955 | 6.4746 | 5.8111 | 5.0225 | 4.4779 | 3.5811
81 | 7.9218 | 7.2145 | 6.5883 | 5.9203 | 5.1289 | 4.5859 | 3.6747
82 | 8.0463 | 7.3341 | 6.7024 | 6.0301 | 5.2361 | 4.6952 | 3.7695
83 | 8.1713 | 7.4542 | 6.8172 | 6.1406 | 5.3443 | 4.8056 | 3.8656
84 | 8.2966 | 7.5748 | 6.9325 | 6.2517 | 5.4533 | 4.9173 | 3.9629
85 | 8.4224 | 7.6959 | 7.0483 | 6.3635 | 5.5632 | 5.0303 | 4.0615
86 | 8.5485 | 7.8174 | 7.1647 | 6.476 | 5.6741 | 5.1444 | 4.1614
87 | 8.6751 | 7.9395 | 7.2817 | 6.5891 | 5.7858 | 5.2598 | 4.2625
88 | 8.802 | 8.062 | 7.3991 | 6.7029 | 5.8984 | 5.3764 | 4.3649
89 | 8.9294 | 8.185 | 7.5172 | 6.8173 | 6.0118 | 5.4942 | 4.4685
90 | 9.0571 | 8.3084 | 7.6357 | 6.9323 | 6.1262 | 5.6132 | 4.5734
91 | 9.1852 | 8.4324 | 7.7548 | 7.048 | 6.2414 | 5.7335 | 4.6796
92 | 9.3137 | 8.5568 | 7.8744 | 7.1643 | 6.3576 | 5.855 | 4.787
93 | 9.4426 | 8.6816 | 7.9945 | 7.2813 | 6.4745 | 5.9777 | 4.8957
94 | 9.5719 | 8.8069 | 8.1151 | 7.3989 | 6.5924 | 6.1016 | 5.0056
95 | 9.7015 | 8.9327 | 8.2363 | 7.5171 | 6.7111 | 6.2268 | 5.1168
96 | 9.8315 | 9.0589 | 8.358 | 7.6359 | 6.8307 | 6.3531 | 5.2293
97 | 9.9619 | 9.1856 | 8.4801 | 7.7553 | 6.9511 | 6.4807 | 5.3431
98 | 10.0926 | 9.3127 | 8.6028 | 7.8754 | 7.0724 | 6.6095 | 5.4581
99 | 10.2237 | 9.4402 | 8.726 | 7.9961 | 7.1945 | 6.7395 | 5.5744
100 | 10.3552 | 9.5682 | 8.8497 | 8.1173 | 7.3175 | 6.8707 | 5.6919
101 | 10.487 | 9.6966 | 8.9739 | 8.2392 | 7.4413 | 7.0031 | 5.8108
102 | 10.6191 | 9.8255 | 9.0985 | 8.3617 | 7.566 | 7.1367 | 5.9309
103 | 10.7517 | 9.9548 | 9.2237 | 8.4848 | 7.6915 | 7.2716 | 6.0523
104 | 10.8845 | 10.0845 | 9.3494 | 8.6085 | 7.8179 | 7.4076 | 6.1749
105 | 11.0177 | 10.2146 | 9.4755 | 8.7328 | 7.9451 | 7.5449 | 6.2989
106 | 11.1513 | 10.3452 | 9.6021 | 8.8576 | 8.0731 | 7.6833 | 6.4241
107 | 11.2852 | 10.4761 | 9.7292 | 8.9831 | 8.202 | 7.823 | 6.5506
108 | 11.4194 | 10.6075 | 9.8568 | 9.1091 | 8.3316 | 7.9639 | 6.6783
109 | 11.554 | 10.7393 | 9.9848 | 9.2357 | 8.4622 | 8.1059 | 6.8074
110 | 11.6889 | 10.8716 | 10.1133 | 9.3629 | 8.5935 | 8.2492 | 6.9377
111 | 11.8242 | 11.0042 | 10.2423 | 9.4907 | 8.7257 | 8.3937 | 7.0693
112 | 11.9598 | 11.1372 | 10.3718 | 9.6191 | 8.8587 | 8.5393 | 7.2022
113 | 12.0957 | 11.2707 | 10.5017 | 9.748 | 8.9925 | 8.6862 | 7.3364
114 | 12.2319 | 11.4045 | 10.6321 | 9.8775 | 9.1271 | 8.8343 | 7.4719
115 | 12.3685 | 11.5388 | 10.7629 | 10.0075 | 9.2625 | 8.9836 | 7.6086
116 | 12.5053 | 11.6734 | 10.8942 | 10.1382 | 9.3987 | 9.134 | 7.7466
117 | 12.6425 | 11.8084 | 11.0259 | 10.2693 | 9.5358 | 9.2857 | 7.886
118 | 12.7801 | 11.9439 | 11.1581 | 10.4011 | 9.6737 | 9.4386 | 8.0266
119 | 12.9179 | 12.0797 | 11.2908 | 10.5334 | 9.8123 | 9.5926 | 8.1685
120 | 13.056 | 12.2159 | 11.4239 | 10.6662 | 9.9518 | 9.7479 | 8.3117